招标说明

说明
QUADRON®185Power Speed
条形 NH 隔离开关熔断器组，尺寸 00
高版，下端连接 M8
CrossLink 连接，带熔丝监测器
185Power

- for vertical and horizontal mounting
- operator independent swichtching mechanism combined with linear operation kinematics
- disconnection of both sides of the NH-contacts (disconnection in front and after the NH-fuses)
- riskless mounting or demounting under voltage without personal protective equipment by using
  the touchprotected busbarsystem and CrossLink®Technology 
  (assessment of the german Employer's Liability Insurance Association)
- plug and play on the busbar system by sticking device with CrossLink-clamp or drilled 
  mounting
- flag indicator shows the switching state via red-green field
- lockable in OFF-position with max. three padlocks
- cover locking with a control panel key
- seal application in ON and OFF position
- all touchable parts are safe by opened cover
- impossible opening of the cover in ON position
- impossible mounting or demounting under load 
  (assessment of the german Employer's Liability Insurance Association)

标准
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

认证许可
IEC (CB)

电气数值
额定电流（IEC）:	160 A
额定电压（IEC）AC:	400 V

AC-23B 160A/400V
AC-23B 160A/400V  

power dissipation at full load of the item:	55.0 W

rated isolation voltage Ui AC:	400 V
额定冲击耐受电压 Uimp:	4 kV

适用熔断器 IEC 60269-2-1 (I) / DIN VDE 0636-201 尺寸1 最大23 W 损耗功率

distance to grounded parts = 0mm at 120kA

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

保护等级 IP30 正面, 取决于安装时的连接区域

其他
When the cover is open, all touchable parts are voltage-free

Operator-independent switching

Lockable cover with double-bit lock

Mixed installation with all components 185Power

Can be sealed when switched on or off

Can be locked with up to 3 padlocks when switched off

品牌
维纳尔或同等价值的产品

订货号
33624000A