招标说明

说明
QUADRON®185Power Speed
条形 NH 隔离开关熔断器组，尺寸 00
标准版，下端连接 M8
螺钉连接
185Power

- for vertical and horizontal mounting
- operator independent swichtching mechanism combined with linear operation kinematics
- disconnection of both sides of the NH-contacts (disconnection in front and after the NH-fuses)
- riskless mounting or demounting under voltage without personal protective equipment by using
  the touchprotected busbarsystem and CrossLink®Technology 
  (assessment of the german Employer's Liability Insurance Association)
- plug and play on the busbar system by sticking device with CrossLink-clamp or drilled 
  mounting
- flag indicator shows the switching state via red-green field
- lockable in OFF-position with max. three padlocks
- cover locking with a control panel key
- seal application in ON and OFF position
- all touchable parts are safe by opened cover
- impossible opening of the cover in ON position
- impossible mounting or demounting under load 
  (assessment of the german Employer's Liability Insurance Association)

标准
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

认证许可
IEC (CB)

电气数值
额定电流（IEC）:	160 A
额定电压（IEC）AC:	800 V
额定电压 （IEC） DC:	800 V

AC-22B (800 V / 63 A)
AC-23B (690 V / 125 A)
AC-23B (500 V / 160 A)

DC-20B
max. voltage between the fuses: 1000 V
visible information required: Do not switch under load.

power dissipation at full load of the item:	55.0 W

rated isolation voltage Ui AC:	1000 V
额定冲击耐受电压 Uimp:	8 kV

适用熔断器 IEC 60269-2-1 (I) / DIN VDE 0636-201 尺寸1 最大23 W 损耗功率

distance to grounded parts = 0mm at 120kA

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

防护等级 IP30 正面, 取决于安装时的连接区域 

原材料性能
壳体:
	耐温性最高 130°C, 
	根据UL 94 有阻燃性, 
	耐蠕变性 CTI 600, 
	不含卤素
触点:
	预压紧弹性铜连接, 镀银   
盖罩:
	耐温性最高 125°C, 
	根据UL 94 有阻燃性, 
	耐蠕变性 CTI 200, 
	不含卤素

其他
When the cover is open, all touchable parts are voltage-free

Operator-independent switching

Lockable cover with double-bit lock

Mixed installation with all components 185Power

Can be sealed when switched on or off

Can be locked with up to 3 padlocks when switched off

品牌
维纳尔或同等价值的产品

订货号
33611000A