招标说明

说明
母线加长连接夹
60 mm
185Power

185Power是具有革新意义的用于电能分配的母线系统, 包括母线系统、用于供电的连接模块/条形连接器,加长连接夹,条形NH-熔断器式隔离开关, 条形NH-隔离开关熔断器组和连接断路器的转接器

通过 Crosslink防触摸保护模块的使用实现185mm母线系统的防触摸保护。

Crosslink 防触摸保护模块的防护等级为IP2X(正面)。
Crosslink防触摸保护带有附加的缝隙盖罩IP4X(正面)

所有的系统部件可以通过挂钩安全、简便、快捷的安装在Crosslink防触摸保护模块上。

30mm,  40mm,  60mm,  80mm,  100mm,  120mm x 10mm的扁平铜母线系统。选择组装的短路稳定性已通过检测。可达到的最大值为: 脉冲峰值电流 Ipk最大105kA/秒,  Icw 最大50kA/秒。 

标准
IEC 61439-1:2011

认证许可
UL

电气数值
额定电压（IEC）AC:	690 V

额定电流 (UL):	1,100 A
额定电压 (UL) AC:	1000 V
额定电压 (UL) DC:	1000 V
最大电流负载能力 (IEC):	1,000 A
最大电压 IEC AC:	1000 V
最大电压 IEC DC:	1500 V

the busbar connector was tested in an arrangment where the busbar supports at the connection of the 2 systems had a spacing of 200 mm

test conditions: 120x10 - 120x10 (2x 01481)
peak withstand current Ipk: 109 kA
Icw (1,0 s): 51 kA

test conditions: 100x10 - 100x10 (1x 01480 + 1x 01481)
peak withstand current Ipk: 106 kA
Icw (1,0 s): 50 kA

test conditions: 60x10 - 60x10 (1x 01481)
peak withstand current Ipk: 81 kA
Icw (1,0 s): 34 kA

品牌
维纳尔或同等价值的产品

订货号
01481000A